Performance Assessment of a UASB Reactor of an Industrial Wastewater Treatment Plant

B. I. Silveira a, M. S. Penafort b, C. D. L. Alves c

a Faculdade de Engenharia Química, Universidade Federal do Pará, inacio@ufpa.br.

b Faculdade de Engenharia Química, Universidade Federal do Pará, menyklen@click21.com.br

c Faculdade de Engenharia Química, Universidade Federal do Pará, charles_denys@yahoo.com.br

Abstract

Wastewaters of beverage industries are rich in carbohydrates, easily biodegradable, and with low suspended solids content. A UASB reactor, characterized by flocculated, compact and decantable granules of methanogenic sludge, has high degradation rate, and is adequate to treat effluents with these characteristics. This work was developed with the main objective of evaluating a UASB reactor performance used as part of an industrial wastewater treatment plant of a beverage industry of medium size. The reactor was monitored by a period of sixty nine days, being evaluated the physiochemical properties of the influent and effluent and the results were expressed as efficiency of the reactor in the COD removal. The results showed that COD in the inlet of the reactor varied between 700 and 2450 mg/L, with an average value of 1520 mg/L and in the exit varied between 12 and 115 mg/L, with an average value of 66 mg/L. The oscillations in the inlet were due to the changes of the organic load of the influent and in the exit it was a function of the reactor efficiency. The pH was evaluated in five point of the reactor content and the averages of these values varied from 6.4 to 6.9, within the range that the methanogenic bacterias have good performance, between 6.0 and 8.0. The temperature within the reactor varied from 28 ºC to 31 ºC, with an average value equal to 30.4 ºC. These data evidenced that the UASB reactor operated in the mesophlic range, between 25 and 40 ºC, and close to the range that is observed the best results of the COD removal efficiency, from 28 ºC to 34 ºC. The values of the COD removal efficiency varied from 90.8 to 98.9%, with an average value of 95.5%. From these results it can be concluded that the pH and temperature stability of the reactor content was decisive in the maintenance of the high efficiency in the COD removal of the system, and that the UASB reactor performance during the monitored period was highly satisfactory in terms of sustainability of an anaerobic treatment system.

Keywords: Wastewater, Efficiency, UASB, COD, Anaerobic treatment.